## DiscreteAlarms
ID | Name | Alarm text [de-DE], Alarm text | FieldInfo [Alarm text] | Class | Trigger tag | Trigger bit | Acknowledgement tag | Acknowledgement bit | PLC acknowledgement tag | PLC acknowledgement bit | Group | Report | Info text [de-DE], Info text
1 | Discrete_alarm_1 | NOT AUS |  | Errors | Main_DB_AlwaysRUN_Alarm_sCvOff | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
2 | Discrete_alarm_2 | Sicherung Ausgänge |  | Errors | Main_DB_AlwaysRUN_Alarm_sFuseOutputsErr | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
3 | Discrete_alarm_3 | Kühlturm 1 Ventilator Störung |  | Errors | Main_DB_AlwaysRUN_Alarm_sCt1FanErr | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
4 | Discrete_alarm_4 | Kühlturm 1 Ventilator Reparaturschalter aus |  | Errors | Main_DB_AlwaysRUN_Alarm_sCt1RepairSwitchOff | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
5 | Discrete_alarm_5 | Kühlturm 2 Ventilator Störung |  | Errors | Main_DB_AlwaysRUN_Alarm_sCt2FanErr | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
6 | Discrete_alarm_6 | Kühlturm 2 Ventilator Reparaturschalter aus |  | Errors | Main_DB_AlwaysRUN_Alarm_sCt2RepairSwitchOff | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
7 | Discrete_alarm_7 | Werkspumpe 1 Störung |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpPlant1Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
8 | Discrete_alarm_8 | Werkspumpe 2 Störung |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpPlant2Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
9 | Discrete_alarm_9 | Kühlwasserpumpe 1 Motorschutzschalter |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpCoolWater1Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
10 | Discrete_alarm_10 | Kühlwasserpumpe 2 Motorschutzschalter |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpCoolWater2Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
11 | Discrete_alarm_11 | Ofenpumpe 1 Motorschutzschalter |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpFurnace1Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
12 | Discrete_alarm_12 | Ofenpumpe 2 Motorschutzschalter |  | Errors | Main_DB_AlwaysRUN_Alarm_sPumpFurnace2Err | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
13 | Discrete_alarm_13 | Vorlauftemperatur Werk zu hoch |  | Errors | Main_DB_AlwaysRUN_Alarm_sFlowTemperaturePlantHot | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
14 | Discrete_alarm_14 | Vorlauftemperatur Ofenkühlung zu hoch |  | Errors | Main_DB_AlwaysRUN_Alarm_sFlowTemperatureFurnaceHot | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
15 | Discrete_alarm_15 | Hebeanlage Filter 1 Differenzdruck zu hoch |  | Errors | Main_DB_AlwaysRUN_Alarm_sPressureDeltaPerc1 | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
16 | Discrete_alarm_16 | Hebeanlage Filter 2 Differenzdruck zu hoch |  | Errors | Main_DB_AlwaysRUN_Alarm_sPressureDeltaPerc2 | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
17 | Discrete_alarm_17 | Wasserstation Ausgleichsbehälter läuft trocken |  | Errors | Main_DB_AlwaysRUN_Alarm_sSurgeTankRunDry | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
18 | Discrete_alarm_18 | Wasserstation Ausgleichsbehälter läuft über |  | Errors | Main_DB_AlwaysRUN_Alarm_sSurgeTankOverflow | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
19 | Discrete_alarm_19 | Kühlturm 1 Sprührohr öffnen Timeout |  | Errors | Main_DB_AlwaysRUN_Alarm_sSprayPipeOpenTimeout1 | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
20 | Discrete_alarm_20 | Kühlturm 2 Sprührohr öffnen Timeout |  | Errors | Main_DB_AlwaysRUN_Alarm_sSprayPipeOpenTimeout2 | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>
21 | Discrete_alarm_21 | Absalzanlage Störung |  | Errors | Main_DB_AlwaysRUN_Alarm_sBleedingUnitErr | 0 | <No value> | 0 | <No value> | 0 | <No value> | True | <No value>

## AnalogAlarms
ID | Name | Alarm text [de-DE], Alarm text | FieldInfo [Alarm text] | Class | Trigger tag | Delay value | Delay time unit | Group | Report | Info text [de-DE], Info text
1 | Analogmeldung_1 | flow temperature too high |  | Warnings | Main_DB_FlowTemperaturePlant | 0 | Millisecond | <No value> | True | <No value>

## Limits
Alarm ID | Limit type | Limit value | Limit mode | Deadband mode | Deadband value | Deadband in percent
1 | Constant | 30 | Upper limit | Off | 0 | False